Date :

| No | Checklist Items |  | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves |  | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure |  | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water |  | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO |  | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH |  | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) |  | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On |  | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby |  | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter |  | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank |  | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor |  | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor |  | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On |  | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby |  | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor |  | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor |  | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity |  | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity |  | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH |  | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) |  | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF |  | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF |  | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room |  | Clean |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |

Date :

| No | Checklist Items | Standard Value | Time : (Shift 1, Shift 2 dan Shift 3) |  |  |  |  |  |  |  | Remark |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 07:30 | 11:30 |  | 15:30 | 19:30 | 23:30 |  | 03:30 |  |  |
| 1 | Piping, Pneumatic hose, Valves | No Leaks |  |  |  |  |  |  |  |  |  |  |
| 2 | Compressed Air Pressure | 0.6-0.8 MPa |  |  |  |  |  |  |  |  |  |  |
| 3 | Availability of cooling water | Available |  |  |  |  |  |  |  |  |  |  |
| 4 | NaCLO | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 5 | NaOH | > 20 L |  |  |  |  |  |  |  |  |  |  |
| 6 | Plant Steam Pressure (on the header) | 3-4 Bar |  |  |  |  |  |  |  |  |  |  |
| 7 | Press. Diff. of 5 Micron Filter Circulation On | ≤ 7 psi |  |  |  |  |  |  |  |  |  |  |
|  | Press. Diff. of 5 Micron Filter Idle/Standby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 8 | UV Lamp Hour Meter | < 8500 h |  |  |  |  |  |  |  |  |  |  |
| 9 | PW Temp. On the PW Tank | ≤ 40 0C |  |  |  |  |  |  |  |  |  |  |
| 10 | PW Temp. On the looping return 1st floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 11 | PW Temp. On the looping return 2nd floor | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 12 | PW Conductivity after EDI Circulation On | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
|  | PW Conductivity after EDI Idle/Stanby | Monitoring Only |  |  |  |  |  |  |  |  |  |  |
| 13 | PW Cond. On the looping return 1st floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 14 | PW Cond. On the looping return 2nd floor | < 1.2 μ/cm |  |  |  |  |  |  |  |  |  |  |
| 15 | PW Loop 1 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 16 | PW Loop 2 Flow Velocity | > 1 m/s |  |  |  |  |  |  |  |  |  |  |
| 17 | pH | 7-9 |  |  |  |  |  |  |  |  |  |  |
| 18 | Soft Water total hardnees (once a day) | < 10 ppm |  |  |  |  |  |  |  |  |  |  |
| 19 | Differential Pressure MMF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 20 | Differential Pressure ACF | < 0.2 MPa |  |  |  |  |  |  |  |  |  |  |
| 21 | Cleanliness of machine and room | Clean |  |  |  |  |  |  |  |  |  |  |
| Notes : PW Conductivity dan PW Conductivity action limit : Sesuai Lampiran SOP/EBI/EN-015-L07 UV Lamp hour meter alert limit : 8000 h, UV Lamp hour meter action limit : 8500 h PW Loop Flow Velocity alert limit : 1.1 m/s, PW Loop Flow Velocity action limit : 1 m/s Pressure Diff. of 5 micron filter alert limit : 6 psi Pressure Diff. of 5 micron filter action limit : 7 psi Pembuatan NaOH dan NaClO mengacu pada SOP/EBI/EN-015. point 7.1.1.2 dan 7.1.1.3. |  |  |  |  | Operator : Shift 1 Shift 2 Shift 3 ( ) ( ) ( ) |  |  |  |  |  |  | Checked By : ( ) |